2021-2022 Results Summary Lead in Water Results School Name: Theodora Smiley Lacey School
Outlet Code
	
Sample ID
	
Location/Description
	Result (ppb)
	Above AL?

1S
	
39-0502-ST01
	
Kitchen 106C - Sink
	
ND
	
No

2BB
	
39-0502-ST02
	
Room 114 - Bubbler
	
ND
	
No

3S
	
39-0502-ST03
	
Room 114 - Sink
	
ND
	
No

4BB
	
39-0502-ST04
	
Room 115 - Bubbler
	
ND
	
No

5S
	
39-0502-ST05
	
Room 115 - Sink
	
ND
	
No

6S
	
39-0502-ST06
	
Room 116 - Sink
	
ND
	
No

7BB
	
39-0502-ST07
	
Room 116 - Bubbler
	
ND
	
No

8BB
	
39-0502-ST08
	
Room 117 - Bubbler
	
ND
	
No

9S
	
39-0502-ST09
	
Room 117 - Sink
	
ND
	
No

10S
	
39-0502-ST10
	
Child Study Room 103 - Sink
	
ND
	
No

11BB
	
39-0502-ST11
	
Child Study Room 103 - Bubbler
	
ND
	
No

12BB
	
39-0502-ST12
	
Nurse's Office - Bubbler
	
ND
	
No

13S
	
39-0502-ST13
	
Nurse's Office - Sink
	
ND
	
No

14BB
	
39-0502-ST14
	
WF/ Filling station at Main Entrance - Bubbler
	
ND
	
No

15BF
	
39-0502-ST15
	
WF/ Filling station at Main Entrance - Filler
	
ND
	
No

16BB
	
39-0502-ST16
	WF/ Filling station in 1st Floor Hallway -Bubbler
	
ND
	
No

17BF
	
39-0502-ST17
	
WF/ Filling station in 1st Floor Hallway - Filler
	
ND
	
No

18S
	
39-0502-ST18
	
Faculty Room 203 - Left tap
	
7.30
	
No

19S
	
39-0502-ST19
	
Faculty Room 203 - Right small tap
	
3.71
	
No

20BB
	
39-0502-ST20
	
Room 205 - Bubbler
	
ND
	
No

Action Level (AL) ≥15.5 parts per billion (ppb)

2021-2022 Results Summary Lead in Water Results School Name: Theodora Smiley Lacey School
Outlet Code
	
Sample ID
	
Location/Description
	Result (ppb)
	Above AL?

21S
	
39-0502-ST21
	
Room 205 - Sink
	
ND
	
No

22S
	
39-0502-ST22
	
Room 206 - Sink
	
ND
	
No

23BB
	
39-0502-ST23
	
Room 206 - Bubbler
	
ND
	
No

24S
	
39-0502-ST24
	
Room 207 - Sink
	
ND
	
No

25BB
	
39-0502-ST25
	
Room 207 - Bubbler
	
ND
	
No

26S
	
39-0502-ST26
	
Room 208 - Sink
	
ND
	
No

27BB
	
39-0502-ST27
	
Room 208 - Bubbler
	
ND
	
No

28BB
	
39-0502-ST28
	WF/ Filling station in 2nd Floor Hallway -Bubbler
	
ND
	
No

29S
	
39-0502-ST29
	
WF/ Filling station in 2nd Floor Hallway - Sink
	
ND
	
No

BLANK
	
39-0502-ST30
	
Field Blank

					

					

					

Action Level (AL) ≥15.5 parts per billion (ppb)

OrderID: 012207022

Page 1 Of	3

OrderID: 012207022

Page 2 Of	3

OrderID: 012207022

Page 3 Of	3

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone: (856) 303-2500	Fax: (856) 858-4571     Email: EnvChemistry2@emsl.com

Attn:	Tom Pruno	5/19/2022 Environmental Design, Inc.
5434 King Avenue Suite 101 Pennsauken, NJ 08109

Phone: (856) 616-9516 Fax:         (586) 616-9517

The following analytical report covers the analysis performed on samples submitted to EMSL Analytical, Inc. on 5/3/2022. The results are tabulated on the attached data pages for the following client designated project:

Teaneck Public Schools - Smiley Theodora Lacey School / Project #: PR-211214-1912

The reference number for these samples is EMSL Order #012207022. Please use this reference when calling about these samples. If you have any questions, please do not hesitate to contact me at (856) 303-2500.

Approved By:

Owen McKenna, Chemistry Laboratory Director

The test results contained within this report meet the requirements of NELAP and/or the specific certification program that is applicable, unless otherwise noted.

NELAP Certifications: NJ 03036, NY 10872, PA 68-00367, CA ELAP 1877

The samples associated with this report were received in good condition unless otherwise noted. This report relates only to those items tested as received by the laboratory. The QC data associated with the sample results meet the recovery and precision requirements established by the NELAP, unless specifically indicated. All results for soil samples are reported on a dry weight basis, unless otherwise noted. This report may not be reproduced except in full and without written approval by EMSL Analytical, Inc.

Page 1 of 8

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207022

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 12:55 PM

Project: Teaneck Public Schools - Smiley Theodora Lacey School / Project #: PR-211214-1912

Client Sample Description	39-0502-ST01

Kitchen 106C - Sink

Analytical Results

Collected:

5/2/2022	Lab ID:	012207022-0001

11:19:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:03

Client Sample Description	39-0502-ST02

Room 114 - Bubbler

Collected:	5/2/2022	Lab ID:	012207022-0002

11:22:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:11

Client Sample Description	39-0502-ST03

Room 114 - Sink

Collected:	5/2/2022	Lab ID:	012207022-0003

11:24:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:12

Client Sample Description	39-0502-ST04

Room 115 - Bubbler

Collected:	5/2/2022	Lab ID:	012207022-0004

11:24:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:14

Client Sample Description	39-0502-ST05

Room 115 - Sink

Collected:	5/2/2022	Lab ID:	012207022-0005

11:25:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:15

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 9:16:22 AM	Page 2 of 8

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207022

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 12:55 PM

Project: Teaneck Public Schools - Smiley Theodora Lacey School / Project #: PR-211214-1912

Client Sample Description	39-0502-ST06

Room 116 Sink

Analytical Results

Collected:

5/2/2022	Lab ID:	012207022-0006

11:26:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:17

Client Sample Description	39-0502-ST07

Room 116 - Bubbler

Collected:	5/2/2022	Lab ID:	012207022-0007

11:27:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:18

Client Sample Description	39-0502-ST08

Room 117 - Bubbler

Collected:	5/2/2022	Lab ID:	012207022-0008

11:26:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:20

Client Sample Description	39-0502-ST09

Room 117 - Sink

Collected:	5/2/2022	Lab ID:	012207022-0009

11:27:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:22

Client Sample Description	39-0502-ST10

Child Study Room 103 - Sink

Collected:	5/2/2022	Lab ID:	012207022-0010

11:30:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:23

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 9:16:22 AM	Page 3 of 8

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207022

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 12:55 PM

Project: Teaneck Public Schools - Smiley Theodora Lacey School / Project #: PR-211214-1912

Analytical Results

Client Sample Description	39-0502-ST11

Child Study Room 103 - Bubbler

Collected:	5/2/2022	Lab ID:	012207022-0011

11:31:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:25

Client Sample Description	39-0502-ST12

Nurse's Office - Bubbler

Collected:	5/2/2022	Lab ID:	012207022-0012

11:29:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:32

Client Sample Description	39-0502-ST13

Nurse's Office - Sink

Collected:	5/2/2022	Lab ID:	012207022-0013

11:30:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:34

Client Sample Description	39-0502-ST14

WF/ Filling Station at Main Entrance - Bubbler

Collected:	5/2/2022	Lab ID:	012207022-0014

11:32:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:36

Client Sample Description	39-0502-ST15

WF/ Filling Station at Main Entrance - Filler

Collected:	5/2/2022	Lab ID:	012207022-0015

11:33:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:37

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 9:16:22 AM	Page 4 of 8

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207022

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 12:55 PM

Project: Teaneck Public Schools - Smiley Theodora Lacey School / Project #: PR-211214-1912

Analytical Results

Client Sample Description	39-0502-ST16

WF/ Filling Station in 1st Floor Hallway - Bubbler

Collected:	5/2/2022	Lab ID:	012207022-0016

11:35:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:39

Client Sample Description	39-0502-ST17

WF/ Filling Station in 1st Floor Hallway - Filler

Collected:	5/2/2022	Lab ID:	012207022-0017

11:36:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:40

Client Sample Description	39-0502-ST18

Faculty Room - Left Tap

Collected:	5/2/2022	Lab ID:	012207022-0018

11:37:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

7.30	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:42

Client Sample Description	39-0502-ST19

Faculty Room - Right Small Tap

Collected:	5/2/2022	Lab ID:	012207022-0019

11:38:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

3.71	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:43

Client Sample Description	39-0502-ST20

Room 205 - Bubbler

Collected:	5/2/2022	Lab ID:	012207022-0020

11:37:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 20:48

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 9:16:22 AM	Page 5 of 8

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207022

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 12:55 PM

Project: Teaneck Public Schools - Smiley Theodora Lacey School / Project #: PR-211214-1912

Client Sample Description	39-0502-ST21

Room 205 - Sink

Analytical Results

Collected:

5/2/2022	Lab ID:	012207022-0021

11:38:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 19:20

Client Sample Description	39-0502-ST22

Room 206 - Sink

Collected:	5/2/2022	Lab ID:	012207022-0022

11:39:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 19:24

Client Sample Description	39-0502-ST23

Room 206 - Bubbler

Collected:	5/2/2022	Lab ID:	012207022-0023

11:40:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 19:26

Client Sample Description	39-0502-ST24

Room 207 - Sink

Collected:	5/2/2022	Lab ID:	012207022-0024

11:41:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 19:27

Client Sample Description	39-0502-ST25

Room 207 - Bubbler

Collected:	5/2/2022	Lab ID:	012207022-0025

11:40:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 19:29

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 9:16:22 AM	Page 6 of 8

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207022

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 12:55 PM

Project: Teaneck Public Schools - Smiley Theodora Lacey School / Project #: PR-211214-1912

Client Sample Description	39-0502-ST26

Room 208 - Sink

Analytical Results

Collected:

5/2/2022	Lab ID:	012207022-0026

11:42:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 19:34

Client Sample Description	39-0502-ST27

Room 208 - Bubbler

Collected:	5/2/2022	Lab ID:	012207022-0027

11:43:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 19:35

Client Sample Description	39-0502-ST28

WF/ Filling Station in 2nd Floor Hallway - Bubbler

Collected:	5/2/2022	Lab ID:	012207022-0028

11:40:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 19:37

Client Sample Description	39-0502-ST29

WF/ Filling Station in 2nd Floor Hallway - Sink

Collected:	5/2/2022	Lab ID:	012207022-0029

11:41:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 19:38

Client Sample Description	39-0502-ST30	Collected:	5/2/2022	Lab ID:	012207022-0030 Field Blank

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 19:40

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 9:16:22 AM	Page 7 of 8

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207022

EDI50

Definitions:

MDL - method detection limit
J - Result was below the reporting limit, but at or above the MDL ND - indicates that the analyte was not detected at the reporting limit RL - Reporting Limit (Analytical)
D - Dilution Sample required a dilution which was used to calculate final results

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 9:16:22 AM	Page 8 of 8