2021-2022 Results Summary Lead in Water Results School Name: Teaneck High School
Outlet Code
	
Sample ID
	
Location/Description
	Result (ppb)
	Above AL?

1WF
	
39-0502-HS01
	
WF inside girl's locker room (right)
	
2.02
	
No

2WF
	
39-0502-HS02
	
WF inside girl's locker room (left)
	
4.19
	
No

4WF
	
39-0502-HS03
	
WF inside boy's locker room (left)
	
5.77
	
No

7WF
	
39-0502-HS04
	
WF next to Rm 114
	
ND
	
No

8WF
	
39-0502-HS05
	
WF - 1st Fl next to stairwell 4/elevator
	
ND
	
No

9WF
	
39-0502-HS06
	
WF next to Rm 100A
	
ND
	
No

10WF
	
39-0502-HS07
	
WF next to Rm 144
	
ND
	
No

11WF
	
39-0502-HS08
	
WF next to Rm 140
	
ND
	
No

16S
	
39-0502-HS09
	
Sink inside Rm 114
	
ND
	
No

17BF
	
39-0502-HS10
	
WF/Filling Station next to Rm 150 (filler)
	
ND
	
No

18BB
	
39-0502-HS11
	
WF/Filling Station next to Rm 150 (bubbler)
	
ND
	
No

19S
	
39-0502-HS12
	
Teacher's Lounge Sink
	
ND
	
No

21BF
	
39-0502-HS13
	
WF/Filler Station in Media Center (filler)
	
ND
	
No

22BB
	
39-0502-HS14
	
WF/Filler Station in Media Center (bubbler)
	
ND
	
No

23WF
	
39-0502-HS15
	
WF next to Rm 238
	
ND
	
No

24WF
	
39-0502-HS16
	
WF next to Principal's office on 2nd Fl
	
1.26
	
No

25WF
	
39-0502-HS17
	
WF near Rm 218
	
10.9
	
No

26WF
	
39-0502-HS18
	
WF across from Rm 344
	
ND
	
No

27S
	
39-0502-HS19
	
Rm 342 (Kitchen sink-corner coffee station)
	
8.42
	
No

28S
	
39-0502-HS20
	
Sink next to oven in kitchen (left side)
	
2.38
	
No

Action Level (AL) ≥15.5 parts per billion (ppb)

2021-2022 Results Summary Lead in Water Results School Name: Teaneck High School
Outlet Code
	
Sample ID
	
Location/Description
	Result (ppb)
	Above AL?

29S
	
39-0502-HS21
	
Rm 332 Teacher Station sink
	
2.95
	
No

30WF
	
39-0502-HS22
	
WF across from Rm 338
	
3.08
	
No

31BF
	
39-0502-HS23
	
WF/Filler Station Rm 300 (filler)
	
ND
	
No

32BB
	
39-0502-HS24
	
WF/Filler Station Rm 300 (bubbler)
	
ND
	
No

33WF
	
39-0502-HS25
	
WF next to Rm 303
	
3.47
	
No

34WF
	
39-0502-HS26
	
WF across from Rm 315
	
ND
	
No

BLANK
	
39-0502-HS27
	
Field Blank
	
ND
	
No

					

					

					

					

Action Level (AL) ≥15.5 parts per billion (ppb)

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone: (856) 303-2500	Fax: (856) 858-4571     Email: EnvChemistry2@emsl.com

Attn:	Tom Pruno	5/19/2022 Environmental Design, Inc.
5434 King Avenue Suite 101 Pennsauken, NJ 08109

Phone: (856) 616-9516 Fax:         (586) 616-9517

The following analytical report covers the analysis performed on samples submitted to EMSL Analytical, Inc. on 5/3/2022. The results are tabulated on the attached data pages for the following client designated project:

Teaneck Public Schools - High School / Project #: PR-211214-1912

The reference number for these samples is EMSL Order #012207108. Please use this reference when calling about these samples. If you have any questions, please do not hesitate to contact me at (856) 303-2500.

Approved By:

Owen McKenna, Chemistry Laboratory Director

The test results contained within this report meet the requirements of NELAP and/or the specific certification program that is applicable, unless otherwise noted.

NELAP Certifications: NJ 03036, NY 10872, PA 68-00367, CA ELAP 1877

The samples associated with this report were received in good condition unless otherwise noted. This report relates only to those items tested as received by the laboratory. The QC data associated with the sample results meet the recovery and precision requirements established by the NELAP, unless specifically indicated. All results for soil samples are reported on a dry weight basis, unless otherwise noted. This report may not be reproduced except in full and without written approval by EMSL Analytical, Inc.

Page 1 of 7

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207108

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 01:00 PM

Project: Teaneck Public Schools - High School / Project #: PR-211214-1912

Analytical Results

Client Sample Description	39-0502-HS01

WF Inside Girl's Locker Room (Right)

Collected:	5/2/2022	Lab ID:	012207108-0001

8:50:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

2.02	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:34

Client Sample Description	39-0502-HS02

WF Inside Girl's Locker Room (Left)

Collected:	5/2/2022	Lab ID:	012207108-0002

8:52:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

4.19	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:38

Client Sample Description	39-0502-HS03

WF Inside Boyl's Locker Room (Left)

Collected:	5/2/2022	Lab ID:	012207108-0003

8:54:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

5.77	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:40

Client Sample Description	39-0502-HS04

WF Next to Rm 1S4

Collected:	5/2/2022	Lab ID:	012207108-0004

9:04:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:42

Client Sample Description	39-0502-HS05

WF - 1st Fl Next to Stairwell 4/Elevator

Collected:	5/2/2022	Lab ID:	012207108-0005

9:13:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:43

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 10:27:29 AM	Page 2 of 7

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207108

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 01:00 PM

Project: Teaneck Public Schools - High School / Project #: PR-211214-1912

Client Sample Description	39-0502-HS06

WF Next to Rm 100A

Analytical Results

Collected:

5/2/2022	Lab ID:	012207108-0006

9:14:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:48

Client Sample Description	39-0502-HS07

WF Next to Rm 114

Collected:	5/2/2022	Lab ID:	012207108-0007

9:15:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:49

Client Sample Description	39-0502-HS08

WF Next to Rm 140

Collected:	5/2/2022	Lab ID:	012207108-0008

9:15:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:51

Client Sample Description	39-0502-HS09

Sink Inside Rm 114

Collected:	5/2/2022	Lab ID:	012207108-0009

9:18:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:52

Client Sample Description	39-0502-HS10

WF/Filling Station Next to Rm 150 (Filler)

Collected:	5/2/2022	Lab ID:	012207108-0010

9:21:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:54

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 10:27:29 AM	Page 3 of 7

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207108

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 01:00 PM

Project: Teaneck Public Schools - High School / Project #: PR-211214-1912

Analytical Results

Client Sample Description	39-0502-HS11

WF/Filling Station Next to Rm 150 (Bubbler)

Collected:	5/2/2022	Lab ID:	012207108-0011

9:22:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:56

Client Sample Description	39-0502-HS12

Teacher's Lounge Sink

Collected:	5/2/2022	Lab ID:	012207108-0012

9:23:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:00

Client Sample Description	39-0502-HS13

WF/Filler Station in Media Center (Filler)

Collected:	5/2/2022	Lab ID:	012207108-0013

9:27:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:02

Client Sample Description	39-0502-HS14

WF/Filler Station in Media Center (Bubbler)

Collected:	5/2/2022	Lab ID:	012207108-0014

9:28:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:06

Client Sample Description	39-0502-HS15

WF Next to Rm 238

Collected:	5/2/2022	Lab ID:	012207108-0015

9:36:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:08

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 10:27:29 AM	Page 4 of 7

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207108

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 01:00 PM

Project: Teaneck Public Schools - High School / Project #: PR-211214-1912

Analytical Results

Client Sample Description	39-0502-HS16

WF Next to Principal's Office on 2nd Fl

Collected:	5/2/2022	Lab ID:	012207108-0016

9:38:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

1.26	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:10

Client Sample Description	39-0502-HS17

WF Near Rm 218

Collected:	5/2/2022	Lab ID:	012207108-0017

9:40:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

10.9	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:11

Client Sample Description	39-0502-HS18

WF Across from Rm 344

Collected:	5/2/2022	Lab ID:	012207108-0018

9:44:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:13

Client Sample Description	39-0502-HS19

Rm 342 (Kitchen Sink-Corner Coffee Station)

Collected:	5/2/2022	Lab ID:	012207108-0019

9:46:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

8.42	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:14

Client Sample Description	39-0502-HS20

Sink Next to Oven in Kitchen (Left Side)

Collected:	5/2/2022	Lab ID:	012207108-0020

9:48:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

2.38	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:16

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 10:27:29 AM	Page 5 of 7

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207108

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 01:00 PM

Project: Teaneck Public Schools - High School / Project #: PR-211214-1912

Client Sample Description	39-0502-HS21

Rm 332 Teacher Station Sink

Analytical Results

Collected:

5/2/2022	Lab ID:	012207108-0021

9:56:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

2.95	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:53

Client Sample Description	39-0502-HS22

WF Across From Rm 338

Collected:	5/2/2022	Lab ID:	012207108-0022

9:57:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

3.08	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:55

Client Sample Description	39-0502-HS23

WF/Filler Station Rm 300 (Filler)

Collected:	5/2/2022	Lab ID:	012207108-0023

9:58:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:56

Client Sample Description	39-0502-HS24

WF/Filler Station Rm 300 (Bubbler)

Collected:	5/2/2022	Lab ID:	012207108-0024

9:57:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:58

Client Sample Description	39-0502-HS25

WF Next to Rm 303

Collected:	5/2/2022	Lab ID:	012207108-0025

9:58:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

3.47	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 14:04

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 10:27:29 AM	Page 6 of 7

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207108

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 01:00 PM

Project: Teaneck Public Schools - High School / Project #: PR-211214-1912

Client Sample Description	39-0502-HS26

WF Across From Rm 315

Analytical Results

Collected:

5/2/2022	Lab ID:	012207108-0026

10:00:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 14:05

Client Sample Description	39-0502-HS27	Collected:	5/2/2022	Lab ID:	012207108-0027 Field Blank

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

Definitions:

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 14:07

MDL - method detection limit
J - Result was below the reporting limit, but at or above the MDL ND - indicates that the analyte was not detected at the reporting limit RL - Reporting Limit (Analytical)
D - Dilution Sample required a dilution which was used to calculate final results

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 10:27:29 AM	Page 7 of 7

OrderID: 012207108

Page 1 Of	3

OrderID: 012207108

Page 2 Of	3

OrderID: 012207108

Page 3 Of	3