2021-2022 Results Summary Lead in Water Results School Name: Lowell Elementary School
Outlet Code
	
Sample ID
	
Location/Description
	Result (ppb)
	Above AL?

1S
	
44-0520-L01
	
Sink inside Kitchen/Cafeteria (Rm 131)
	
2.46
	
No

2BF
	
44-0520-L02
	
WF/Filling Station (filler)
	
ND
	
No

3BB
	
44-0520-L03
	
WF/Filling Station (bubbler)
	
ND
	
No

4S
	
44-0520-L04
	
Sink inside Teacher's Lounge (Rm 120)
	
ND
	
No

5WF
	
44-0520-L05
	
WF outside Rm 115
	
19.6
	
Yes

6WF
	
44-0520-L06
	
WF next to Rm 101
	
2.65
	
No

7WF
	
44-0520-L07
	
Water Room next to Rm 201
	
3.00
	
No

8WF
	
44-0520-L08
	
WF next to Rm 212
	
6.25
	
No

9BF
	
44-0520-L09
	
WF/Filling Station (filler) across from Rm 227
	
ND
	
No

10BB
	
44-0520-L10
	WF/Filling Station (bubbler) across from Rm 227
	
ND
	
No

BLANK
	
44-0502-L11
	
Field Blank
	
ND
	
No

5WF
	
58-0609-L01
	Retesting WF Bubbler Outside Room 115 -Water fountain
	
ND
	
No

11BF
	
58-0609-L02
	
BF Bubbler Outside Room 115 - Bottle filler
	
ND
	
No

BLANK
	
58-0609-L03
	
DI Blank
	
ND
	
No

					

					

Action Level (AL) ≥15.5 parts per billion (ppb)

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone: (856) 303-2500	Fax: (856) 858-4571     Email: EnvChemistry2@emsl.com

Attn:	Tom Pruno	5/19/2022 Environmental Design, Inc.
5434 King Avenue Suite 101 Pennsauken, NJ 08109

Phone: (856) 616-9516 Fax:         (586) 616-9517

The following analytical report covers the analysis performed on samples submitted to EMSL Analytical, Inc. on 5/3/2022. The results are tabulated on the attached data pages for the following client designated project:

Teaneck Public Schools - Lowell Elementary School / PR-211214-1912

The reference number for these samples is EMSL Order #012207111. Please use this reference when calling about these samples. If you have any questions, please do not hesitate to contact me at (856) 303-2500.

Approved By:

Owen McKenna, Chemistry Laboratory Director

The test results contained within this report meet the requirements of NELAP and/or the specific certification program that is applicable, unless otherwise noted.

NELAP Certifications: NJ 03036, NY 10872, PA 68-00367, CA ELAP 1877

The samples associated with this report were received in good condition unless otherwise noted. This report relates only to those items tested as received by the laboratory. The QC data associated with the sample results meet the recovery and precision requirements established by the NELAP, unless specifically indicated. All results for soil samples are reported on a dry weight basis, unless otherwise noted. This report may not be reproduced except in full and without written approval by EMSL Analytical, Inc.

Page 1 of 4

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207111

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 12:50 PM

Project: Teaneck Public Schools - Lowell ElementarySchool / PR-211214-1912

Analytical Results

Client Sample Description	44-0520-L01

Sink Inside Kitchen/Cafeteria (Rm 131)

Collected:	5/2/2022	Lab ID:	012207111-0001

12:54:00 PM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

2.46	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:00

Client Sample Description	44-0520-L02

WF/Filling Station (Filler)

Collected:	5/2/2022	Lab ID:	012207111-0002

12:58:00 PM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:04

Client Sample Description	44-0520-L03

WF/Filling Station (Bubbler)

Collected:	5/2/2022	Lab ID:	012207111-0003

12:59:00 PM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:06

Client Sample Description	44-0520-L04

Sink Inside Teacher's Lounge (Rm 120)

Collected:	5/2/2022	Lab ID:	012207111-0004

1:00:00 PM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:10

Client Sample Description	44-0520-L05

WF Next to Rm 115

Collected:	5/2/2022	Lab ID:	012207111-0005

1:01:00 PM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

19.6	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:12

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 10:31:42 AM	Page 2 of 4

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207111

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 12:50 PM

Project: Teaneck Public Schools - Lowell ElementarySchool / PR-211214-1912

Client Sample Description	44-0520-L06

WF Next to Rm 101

Analytical Results

Collected:

5/2/2022	Lab ID:	012207111-0006

1:03:00 PM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

2.65	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:14

Client Sample Description	44-0520-L07

Water Room Next to Rm 201

Collected:	5/2/2022	Lab ID:	012207111-0007

1:10:00 PM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

3.00	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:15

Client Sample Description	44-0520-L08

WF Next to Rm 212

Collected:	5/2/2022	Lab ID:	012207111-0008

1:11:00 PM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

6.25	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:17

Client Sample Description	44-0520-L09

WF/Filling Station (Filler) Across From Rm 227

Collected:	5/2/2022	Lab ID:	012207111-0009

1:13:00 PM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:18

Client Sample Description	44-0520-L10

WF/Filling Station (Bubbler) Across From Rm 227

Collected:	5/2/2022	Lab ID:	012207111-0010

1:14:00 PM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:20

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 10:31:42 AM	Page 3 of 4

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207111

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 12:50 PM

Project: Teaneck Public Schools - Lowell ElementarySchool / PR-211214-1912

Client Sample Description	44-0520-L11

Field Blank

Analytical Results

Collected:	5/2/2022	Lab ID:	012207111-0011

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

Definitions:

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 12:21

MDL - method detection limit
J - Result was below the reporting limit, but at or above the MDL ND - indicates that the analyte was not detected at the reporting limit RL - Reporting Limit (Analytical)
D - Dilution Sample required a dilution which was used to calculate final results

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 10:31:42 AM	Page 4 of 4

OrderID: 012207111

Page 1 Of	1

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone: (856) 303-2500	Fax: (856) 858-4571     Email: EnvChemistry2@emsl.com

Attn:	Tom Pruno	6/21/2022 Environmental Design, Inc.
5434 King Avenue Suite 101 Pennsauken, NJ 08109

Phone: (856) 616-9516 Fax:         (586) 616-9517

The following analytical report covers the analysis performed on samples submitted to EMSL Analytical, Inc. on 6/10/2022. The results are tabulated on the attached data pages for the following client designated project:

Teaneck BOE - Lowell E.S. Re-sampling / Project #: PR-211214-1912

The reference number for these samples is EMSL Order #012209158. Please use this reference when calling about these samples. If you have any questions, please do not hesitate to contact me at (856) 303-2500.

Approved By:

Owen McKenna, Chemistry Laboratory Director

The test results contained within this report meet the requirements of NELAP and/or the specific certification program that is applicable, unless otherwise noted.

NELAP Certifications: NJ 03036, NY 10872, PA 68-00367, CA ELAP 1877

The samples associated with this report were received in good condition unless otherwise noted. This report relates only to those items tested as received by the laboratory. The QC data associated with the sample results meet the recovery and precision requirements established by the NELAP, unless specifically indicated. All results for soil samples are reported on a dry weight basis, unless otherwise noted. This report may not be reproduced except in full and without written approval by EMSL Analytical, Inc.

Page 1 of 2

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012209158

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
06/10/22 11:50 AM

Project: Teaneck BOE - Lowell E.S. Re-sampling / Project #: PR-211214-1912

Client Sample Description	58-0609-L01

WF Bubbler Outside Room 115

Analytical Results

Collected:

6/9/2022	Lab ID:	012209158-0001

6:47:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead	ND	1.00 µg/L	6/20/2022	VD	06/20/22 13:14     VD

Client Sample Description	58-0609-L02

BF Bubbler Outside Room 115

Collected:	6/9/2022	Lab ID:	012209158-0002

6:47:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead	ND	1.00 µg/L	6/20/2022	VD	06/20/22 13:19     VD

Client Sample Description	58-0609-L03	Collected:	Lab ID:	012209158-0003 DI Water Blank

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead	ND	1.00 µg/L	6/20/2022	VD	06/20/22 13:21     VD

Definitions:

MDL - method detection limit

J - Result was below the reporting limit, but at or above the MDL ND - indicates that the analyte was not detected at the reporting limit RL - Reporting Limit (Analytical)
D - Dilution Sample required a dilution which was used to calculate final results

ChemSmplw/RDL/NELAC-7.52.0 Printed: 6/21/2022 7:01:14 PM	Page 2 of 2

OrderID: 012209158

Page 1 Of	1