2021-2022 Results Summary Lead in Water Results School Name: Thomas Jefferson Middle School
Outlet Code
	
Sample ID
	
Location/Description
	Result (ppb)
	Above AL?

1BF
	
39-0502-TJ01
	
WF/Filling Station in cafeteria (filler)
	
ND
	
No

2BB
	
39-0502-TJ02
	
WF/Filling Station in cafeteria (bubbler)
	
ND
	
No

3WF
	
39-0502-TJ03
	
WF in cafeteria
	
2.67
	
No

4WF
	
39-0502-TJ04
	
WF outside girl's locker room
	
ND
	
No

5WF
	
39-0502-TJ05
	
WF inside girl's locker room
	
22.9
	
Yes

6WF
	
39-0502-TJ06
	
WF inside boy's locker room
	
2.35
	
No

7WF
	
39-0502-TJ07
	
WF next to custodial room
	
14
	
No

10WF
	
39-0502-TJ08
	
WF across from main/attendance office
	
26.4
	
Yes

11WF
	
39-0502-TJ09
	
WF across from Rm 107
	
2.59
	
No

14WF
	
39-0502-TJ10
	
WF across from library
	
82.8
	
Yes

15WF
	
39-0502-TJ11
	
WF next to Rm 214
	
1.96
	
No

BLANK
	
39-0502-TJ12
	
Field Blank
	
ND
	
No

16BF
	
56-0609-TJ01
	
BF Inside Girl's Locker Room
	
ND
	
No

5WF
	
56-0609-TJ02
	
Restesting WF Inside Girl's Locker Room
	
ND
	
No

17BF
	
56-0609-TJ03
	
BF across from main office
	
ND
	
No

10WF
	
56-0609-TJ04
	
Restesting WF Bubbler across from main office
	
ND
	
No

18BF
	
56-0609-TJ05
	
BF across from library
	
ND
	
No

14WF
	
56-0609-TJ06
	
Restesting WF across from library
	
ND
	
No

BLANK
	
56-0609-TJ07
	
Restesting DI Blank
	
ND
	
No

Action Level (AL) ≥15.5 parts per billion (ppb)

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone: (856) 303-2500	Fax: (856) 858-4571     Email: EnvChemistry2@emsl.com

Attn:	Tom Pruno	5/19/2022 Environmental Design, Inc.
5434 King Avenue Suite 101 Pennsauken, NJ 08109

Phone: (856) 616-9516 Fax:         (586) 616-9517

The following analytical report covers the analysis performed on samples submitted to EMSL Analytical, Inc. on 5/3/2022. The results are tabulated on the attached data pages for the following client designated project:

Teaneck Public Schools - Thomas Jefferson MIddle School / Project #: PR-211214-1912

The reference number for these samples is EMSL Order #012207105. Please use this reference when calling about these samples. If you have any questions, please do not hesitate to contact me at (856) 303-2500.

Approved By:

Owen McKenna, Chemistry Laboratory Director

The test results contained within this report meet the requirements of NELAP and/or the specific certification program that is applicable, unless otherwise noted.

NELAP Certifications: NJ 03036, NY 10872, PA 68-00367, CA ELAP 1877

The samples associated with this report were received in good condition unless otherwise noted. This report relates only to those items tested as received by the laboratory. The QC data associated with the sample results meet the recovery and precision requirements established by the NELAP, unless specifically indicated. All results for soil samples are reported on a dry weight basis, unless otherwise noted. This report may not be reproduced except in full and without written approval by EMSL Analytical, Inc.

Page 1 of 4

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207105

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 01:00 PM

Project: Teaneck Public Schools - Thomas Jefferson MIddle School / Project #: PR-211214-1912

Analytical Results

Client Sample Description	39-0502-TJ01

WF/Filling Station in Cafeteria (Filler)

Collected:	5/2/2022	Lab ID:	012207105-0001

10:35:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:25

Client Sample Description	39-0502-TJ02

WF/Filling Station in Cafeteria (Bubbler)

Collected:	5/2/2022	Lab ID:	012207105-0002

10:36:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:30

Client Sample Description	39-0502-TJ03

WF in Cafeteria

Collected:	5/2/2022	Lab ID:	012207105-0003

10:37:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

2.67	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:31

Client Sample Description	39-0502-TJ04

WF Outside Girl's Locker Room

Collected:	5/2/2022	Lab ID:	012207105-0004

10:39:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:33

Client Sample Description	39-0502-TJ05

WF Inside Girl's Locker Room

Collected:	5/2/2022	Lab ID:	012207105-0005

10:40:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

22.9	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:34

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 10:23:29 AM	Page 2 of 4

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207105

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 01:00 PM

Project: Teaneck Public Schools - Thomas Jefferson MIddle School / Project #: PR-211214-1912

Client Sample Description	39-0502-TJ06

WF Inside Boy's Locker Room

Analytical Results

Collected:

5/2/2022	Lab ID:	012207105-0006

10:42:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

2.35	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:36

Client Sample Description	39-0502-TJ07

WF Next to Custodial Room

Collected:	5/2/2022	Lab ID:	012207105-0007

10:45:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

14.0	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:38

Client Sample Description	39-0502-TJ08

WF Across from Main/Attendance Office

Collected:	5/2/2022	Lab ID:	012207105-0008

10:49:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

26.4	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:39

Client Sample Description	39-0502-TJ09

WF Across from Rm 107

Collected:	5/2/2022	Lab ID:	012207105-0009

10:51:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

2.59	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:44

Client Sample Description	39-0502-TJ10

WF Across from Library

Collected:	5/2/2022	Lab ID:	012207105-0010

10:55:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

82.8	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:45

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 10:23:29 AM	Page 3 of 4

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012207105

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
5/3/2022 01:00 PM

Project: Teaneck Public Schools - Thomas Jefferson MIddle School / Project #: PR-211214-1912

Client Sample Description	39-0502-TJ11

WF Next to Rm 214

Analytical Results

Collected:

5/2/2022	Lab ID:	012207105-0011

10:57:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

1.96	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:47

Client Sample Description	39-0502-TJ12	Collected:	5/2/2022	Lab ID:	012207105-0012 Field Blank

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead

Definitions:

ND	1.00 µg/L	5/16/2022	VD	5/17/2022	VD 13:52

MDL - method detection limit
J - Result was below the reporting limit, but at or above the MDL ND - indicates that the analyte was not detected at the reporting limit RL - Reporting Limit (Analytical)
D - Dilution Sample required a dilution which was used to calculate final results

ChemSmplw/RDL/NELAC-2.19.0.0 Printed: 5/19/2022 10:23:29 AM	Page 4 of 4

OrderID: 012207105

Page 1 Of	1

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone: (856) 303-2500	Fax: (856) 858-4571     Email: EnvChemistry2@emsl.com

Attn:	Tom Pruno	6/21/2022 Environmental Design, Inc.
5434 King Avenue Suite 101 Pennsauken, NJ 08109

Phone: (856) 616-9516 Fax:         (586) 616-9517

The following analytical report covers the analysis performed on samples submitted to EMSL Analytical, Inc. on 6/10/2022. The results are tabulated on the attached data pages for the following client designated project:

Teaneck BOE - Thomas Jefferson M.S. Re-sampling / Project #: PR-211214-1912

The reference number for these samples is EMSL Order #012209162. Please use this reference when calling about these samples. If you have any questions, please do not hesitate to contact me at (856) 303-2500.

Approved By:

Owen McKenna, Chemistry Laboratory Director

The test results contained within this report meet the requirements of NELAP and/or the specific certification program that is applicable, unless otherwise noted.

NELAP Certifications: NJ 03036, NY 10872, PA 68-00367, CA ELAP 1877

The samples associated with this report were received in good condition unless otherwise noted. This report relates only to those items tested as received by the laboratory. The QC data associated with the sample results meet the recovery and precision requirements established by the NELAP, unless specifically indicated. All results for soil samples are reported on a dry weight basis, unless otherwise noted. This report may not be reproduced except in full and without written approval by EMSL Analytical, Inc.

Page 1 of 3

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012209162

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
06/10/22 11:55 AM

Project: Teaneck BOE - Thomas Jefferson M.S. Re-sampling / Project #: PR-211214-1912

Client Sample Description	58-0609-TJ01

BF Inside Girl's Locker Room

Analytical Results

Collected:

6/9/2022	Lab ID:	012209162-0001

6:20:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead	ND	1.00 µg/L	6/20/2022	VD	06/20/22 13:25     VD

Client Sample Description	58-0609-TJ02

WF Bubbler Inside Girl's Locker Room

Collected:	6/9/2022	Lab ID:	012209162-0002

6:20:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead	ND	1.00 µg/L	6/20/2022	VD	06/20/22 13:27     VD

Client Sample Description	58-0609-TJ03

BF Across From Main Office

Collected:	6/9/2022	Lab ID:	012209162-0003

6:26:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead	ND	1.00 µg/L	6/20/2022	VD	06/20/22 13:28     VD

Client Sample Description	58-0609-TJ04

WB Bubbler Across from Main Office

Collected:	6/9/2022	Lab ID:	012209162-0004

6:26:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead	ND	1.00 µg/L	6/20/2022	VD	06/20/22 13:30     VD

Client Sample Description	58-0609-TJ05

BF Across from Library

Collected:	6/9/2022	Lab ID:	012209162-0005

6:29:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead	ND	1.00 µg/L	6/20/2022	VD	06/20/22 13:32     VD

ChemSmplw/RDL/NELAC-7.52.0 Printed: 6/21/2022 7:02:39 PM	Page 2 of 3

EMSL Analytical, Inc.

200 Route 130 North, Cinnaminson, NJ 08077

Phone/Fax:	(856) 303-2500 / (856) 858-4571 http://www.EMSL.com                             EnvChemistry2@emsl.com

EMSL Order: CustomerID: CustomerPO:
ProjectID:

012209162

EDI50

Attn: Tom Pruno
Environmental Design, Inc. 5434 King Avenue
Suite 101 Pennsauken, NJ 08109

Phone: Fax:
Received:

(856) 616-9516 (586) 616-9517
06/10/22 11:55 AM

Project: Teaneck BOE - Thomas Jefferson M.S. Re-sampling / Project #: PR-211214-1912

Analytical Results

Client Sample Description	58-0609-TJ06

WF Bubbler Across From Library

Collected:	6/9/2022	Lab ID:	012209162-0006

6:29:00 AM

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead	ND	1.00 µg/L	6/20/2022	VD	06/20/22 13:33     VD

Client Sample Description	58-0609-TJ07	Collected:	Lab ID:	012209162-0007 DI Water Blank

Prep Method	Parameter	Result	RL Units	Date & Analyst

Analysis Date & Analyst

METALS

200.8	Lead	ND	1.00 µg/L	6/20/2022	VD	06/20/22 13:35     VD

Definitions:

MDL - method detection limit
J - Result was below the reporting limit, but at or above the MDL ND - indicates that the analyte was not detected at the reporting limit RL - Reporting Limit (Analytical)
D - Dilution Sample required a dilution which was used to calculate final results

ChemSmplw/RDL/NELAC-7.52.0 Printed: 6/21/2022 7:02:39 PM	Page 3 of 3

OrderID: 012209162

Page 1 Of	1